## Sayfa1
Profinet Status ve Control Word bit konfigürasyonu
Status Word |  |  |  | Control Word
Bit no | 0 | 1 |  | Bit no | 0 | 1
0 | Control Not Ready | Control Ready | 1 | 0 | OFF 1 | ON 1 | 1
1 | Drive not Ready | Drive Ready | 1 | 1 | OFF 2 | ON 2 | 1
2 | Coasting | Enable | 1 | 2 | OFF 3 | ON 3 | 1
3 | No Error | Trip | 1 | 3 | Coasting | No Coasting | 1
4 | OFF 2 | ON2 | 1 | 4 | Quick Stop | Ramp | 1
5 | OFF 3 | ON3 | 1 | 5 | Hold Frequency Output | Use Ramp | 1
6 | Start Possible | Start not Possible | 1 | 6 | Ramp Stop | Start | 1
7 | No Warning | Warning | 1 | 7 | No Function | Reset | 0
8 | Speed not reference | Speed = Reference | 1 | 8 | Jog 1 Off | Jog 1 On | 0
9 | Lokal Operation | Bus Control | 1 | 9 | Jog 2 Off | Jog 2 On | 0
10 | Out of frequency limit | Frequency limit OK | 1 | 10 | Data Invalid | Data Valid | 1
11 | No Operation | In Operation | 1 | 11 | No Function | Slow Down | 0
12 | Driver OK | Stopped, Autostart | 1 | 12 | No Function | Catch Up | 0
13 | Voltage OK | Voltage exceeded | 1 | 13 | Parameter Set-up | Selection lsb | 0
14 | Torque | Torque exceeded | 0 | 14 | Parameter Set-up | Selection lsb | 0
15 | Timer OK | Timer exceeded | 1 | 15 | No Function | Reverse | 0
Decimal |  | 49151 |  | Decimal |  | 1151
Hex |  | BFFF |  | Hex |  | 47F
DeviceNet Status ve Control Word bit konfigürasyonu
Status Word |  |  |  | Control Word
Bit no | 0 | 1 |  | Bit no | 0 | 1
0 | Kontrol hazır değil | Kontrol Hazır | 1 | 0 | Preset Referans seçimi 0 | Preset Referans seçimi 0 | 1
1 | VLT Hazır Değil | VLT Hazır | 1 | 1 | Preset Referans seçimi 1 | Preset Referans seçimi 1 | 1
2 | Serbest Duruş | Aktif | 1 | 2 | DC Fren | Rampa Aktif | 1
3 | Hata Yok | Trip Konumunda | 1 | 3 | Serbest Duruş | Serbest Duruş Yok | 1
4 | Hata Yok | Hata | 1 | 4 | Hızlı Durdurma | Hızlı Durdurma Yok | 1
5 | Rezerve | - | 1 | 5 | Çıkış Frekansını Tut | Rampalı Duruş | 1
6 | Hata Yok | Trip Konumunda ve Kilitli | 1 | 6 | Rampa Stop | Start | 1
7 | Uyarı Yok | Uyarı Var | 1 | 7 | Fonksiyon yok | Reset | 1
8 | İstenen Frekansa Ulaşılmadı | İstenen Frekansa Ulaşıldı | 1 | 8 | Fonksiyon yok | Jog | 1
9 | Lokal Kontrol | Bus kontrol | 1 | 9 | Rampa 1 | Rampa 2 | 1
10 | Frekans Limiti Dışı | Frekans Limiti OK | 1 | 10 | Data izni yok | Data izni | 1
11 | FC çalışmıyor | FC çalışıyor | 1 | 11 | Fonksiyon yok | Röle 1 Aktif | 1
12 | Driver OK | Durdu, Otomatik Start | 0 | 12 | Fonksiyon yok | Röle 2 Aktif | 1
13 | Voltage OK | Voltage Aşıldı | 1 | 13 | Parametre Set-up | Bit-0 | 1
14 | Tork OK | Tork Aşıldı | 1 | 14 | Parametre Set-up | Bit-1 | 0
15 | Timer OK | Zaman Aşıldı | 1 | 15 | Fonksiyon yok | Rezerve | 1
Decimal |  | 61439 |  | Decimal |  | 49151
Hex |  | EFFF |  | Hex |  | BFFF
ProfiBus Status ve Control Word bit konfigürasyonu
Status Word |  |  |  | Control Word
Bit no | 0 | 1 | 1 | Bit no | 0 | 1
0 | Control Not Ready | Control Ready | 1 | 0 | OFF 1 | ON 1 | 1
1 | Drive not Ready | Drive Ready | 1 | 1 | OFF 2 | ON 2 | 1
2 | Coasting | Enable | 1 | 2 | OFF 3 | ON 3 | 1
3 | No Error | Trip | 1 | 3 | Coasting | No Coasting | 1
4 | OFF 2 | ON2 | 1 | 4 | Quick Stop | Ramp | 1
5 | OFF 3 | ON3 | 1 | 5 | Hold Frequency Output | Use Ramp | 1
6 | Start Possible | Start not Possible | 1 | 6 | Ramp Stop | Start | 1
7 | No Warning | Warning | 1 | 7 | No Function | Reset | 1
8 | Speed not reference | Speed = Reference | 1 | 8 | Jog 1 Off | Jog 1 On | 1
9 | Lokal Operation | Bus Control | 1 | 9 | Jog 2 Off | Jog 2 On | 1
10 | Out of frequency limit | Frequency limit OK | 1 | 10 | Data Invalid | Data Valid | 1
11 | No Operation | In Operation | 0 | 11 | No Function | Slow Down | 1
12 | Driver OK | Stopped, Autostart | 1 | 12 | No Function | Catch Up | 1
13 | Voltage OK | Voltage exceeded | 1 | 13 | Parameter Set-up | Selection lsb | 1
14 | Torque | Torque exceeded | 1 | 14 | Parameter Set-up | Selection lsb | 0
15 | Timer OK | Timer exceeded | 1 | 15 | No Function | Reverse | 1
Decimal |  | 63487 |  | Decimal |  | 49151
Hex |  | F7FF |  | Hex |  | BFFF
ModBus Status ve Control Word bit konfigürasyonu
Status Word |  |  |  | Control Word
Bit no | 0 | 1 |  | Bit no | 0 | 1
0 | Control Not Ready | Control Ready | 0 | 0 | Reference Value | External Selection lsb | 0
1 | Drive not Ready | Drive Ready | 1 | 1 | Reference Value | External Selection msb | 0
2 | Coasting | Enable | 1 | 2 | DC Brake | Ramp | 1
3 | No Error | Trip | 1 | 3 | Coasting | No Coasting | 1
4 | No Error | Error ( No Trip) | 1 | 4 | Quick Stop | Ramp | 1
5 | Reserved | - | 1 | 5 | Hold Output Frequency | Use Ramp | 1
6 | No Error | Trip Lock | 1 | 6 | Ramp Stop | Start | 0
7 | No Warning | Warning | 1 | 7 | No function | Reset | 0
8 | Speed not reference | Speed = Reference | 1 | 8 | No function | Jog | 0
9 | Lokal Operation | Bus Control | 1 | 9 | Ramp 1 | Ramp 2 | 0
10 | Out of frequency limit | Frequency limit OK | 1 | 10 | Data İnvalid | Data İnvalid | 1
11 | No Operation | In Operation | 1 | 11 | Relay 01 Open | Relay 01 active | 0
12 | Driver OK | Stopped, Autostart | 1 | 12 | Relay 02 Open | Relay 02 active | 0
13 | Voltage OK | Voltage exceeded | 1 | 13 | Parameter Set-Up | Selection lsb | 0
14 | Torque | Torque exceeded | 1 | 14 | ------------------------------ | -------------------------- | 0
15 | Timer OK | Timer exceeded | 1 | 15 | No function | Reverse | 0
Decimal |  | 65534 |  | Decimal |  | 1084
Hex |  | FFFE |  | Hex |  | 43C
EtherCat Status ve Control Word bit konfigürasyonu
Status Word |  |  |  | Control Word
Bit no | 0 | 1 |  | Bit no | 0 | 1
0 | Not Ready to switch ON | Ready to switch ON | 1 | 0 | Switch Off | Switch On | 0
1 | Switched OFF | Switched ON | 1 | 1 | Disable Voltage | Enable Voltage | 0
2 | Operation disabled | Operation Enabled | 0 | 2 | Quick Stop | Run | 1
3 | No Malfunction | Malfunction | 1 | 3 | Disable Operation | Enable Operation | 1
4 | Voltage Disabled | Voltage Enabled | 0 | 4 | Disable Ramp | Enable Ramp | 1
5 | Quick Stop | Run | 1 | 5 | Freeze | Run Enable | 1
6 | Switch On disable | Switch on enable | 1 | 6 | Ramp Stop | Start | 1
7 | No warning | Warning | 0 | 7 | No Function | Reset | 0
8 | Reserved | Reserved | 0 | 8 | Reserved | Reserved | 0
9 | Remote disabled | Remote enabled | 1 | 9 | Reserved | Reserved | 0
10 | Set Point Not Reached | Set Point Reached | 1 | 10 | Reserved | Reserved | 1
11 | Speed Limit Not Active | Speed Limit Active | 1 | 11 | Jog 1 OFF | Jog 1 ON | 0
12 | Reserved | Reserved | 1 | 12 | Reserved | Reserved | 0
13 | Reserved | Reserved | 0 | 13 | Parameter Set-up | Selection lsb | 0
14 | Not Running | Running | 1 | 14 | Parameter Set-up | Selection lsb | 0
15 | Reserved | Reserved | 1 | 15 | Forward | Reversing | 0
Decimal |  | 56939 |  | Decimal |  | 1148
Hex |  | DE6B |  | Hex |  | 47C